## Checklist
Time(hours) | WCRCS/NSRS Validation Checklist |  |  |  | Does this protect WCRCS/NSRS? | Comments
Organization:
| No. | Title | Value (or ✓ / Yes / No / N/A) | Pass/Fail
| 1 | Statement of Purpose: Allow XXXX to transmit again witin the Washoe County. (WCRCS being the Authority having jurisdiction)
| 1.1 | Performance of the procedures outlined in this checklist serves to validate the operation of DAS on NSRS system- SITE : . Satisfaction of the testing requirements permits the excution of the rebroadcast agreement.
| 2 | Sequence:
| 2.1 | • DAS Inventory and Documentation(X-digital) • Isolation Testing(X) • DL Testing(X) • Donor Site UL Testing • BDA UL Testing(X) • TDI Testing • Sign-off(X)
| 3 | Required tools and materials:
| 3.1 | • 2 configured portable test radios (X) • Calibrated spectrum analyzer (X) • Portable radio test antenna for spectrum analyzer(X) • RF test jumper (X) • Signal generator • 5W 20dB attenuator(X) • RF adapter kit (X) • Laptop computer (X) • Ethernet Cable(X) • Crossover cable adapter(X)
| 4 | Table of Values:
1 | 4.1 | Inventory:
| 4.1.1 | BDA location
| 4.1.2 | BDA model
| 4.1.3 | BDA firmware
| 4.1.4 | Vendor confirms all DAS antennas connected
| 4.1.5 | Fiber infrastructure make and model
| 4.1.6 | Number of fiber remotes
| 4.1.7 | Donor antenna location
| 4.1.8 | Donor antenna type
| 4.1.9 | Donor antenna gain (indicate dBd or dBi)
| 4.1.10 | Max ERP from donor antenna
| 4.1.11 | Donor antenna azimuth
| 4.1.12 | Expected donor site
| 4.1.13 | Inline attenuator value
1 | 4.2 | BDA Configuration:
| 4.2.1 | Verify filters
| 4.2.2 | Configured DL gain
| 4.2.3 | Configured UL gain
| 4.2.4 | Verify UL AGC/ALC
| 4.2.5 | Verify UL squelch configured
0.5 | 4.3 | Isolation
| 4.3.1 | Isolation Results
0.5 | 4.4 | DL Testing
| 4.4.1 | DL receive at BDA donor input
| 4.4.2 | Calculated path loss from donor site
| 4.4.3 | BDA DL output
1 | 4.5 | Donor site UL testing
| 4.5.1 | RX noise floor value with DAS off
| 4.5.2 | BDA on/off test to verify no noise rise
| 4.5.3 | Max UL receive
| 4.5.4 | Min UL receive
1 | 4.6 | DAS UL testing
| 4.6.1 | Measure max UL input to BDA
| 4.6.2 | Measure min UL input to BDA
| 4.6.3 | Measure max UL output of BDA (verifying AGC)
| 4.6.4 | Measure min UL output of BDA
| 4.6.5 | Measure UL squelch
| 4.6.6 | Expected noise RX at donor site
| 4.6.6 | Estimate max UL receive at donor site with calculated path loss
| 4.6.7 | Estimate min UL receive at donor site with calculated path loss
1 | 4.7 | TDI testing
| 4.7.1 | Comms check 3', 15', 30' from all emergency egress
| 4.7.2 | Test channel signal strength at 3' if 4.7.1 failure
0.5 | 5 | Technician Sign-off
| 5.1 | DAS vendor point of contact name
| 5.2 | DAS vendor point of contact email
| 5.3 | Radio operator technician name
| 5.4 | Date
| 6 | Procedure for Rebroadcast Agreement execution
Total=
6.5

## Procedure
4.1 | Inventory: |  | Comments:
4.1.1 | BDA location | Document floor, room number, any supplemental info to find and access DAS BDA
4.1.2 | BDA model | Document BDA model number
4.1.3 | BDA firmware | If available, document installed firmware version(s)
4.1.4 | Vendor confirms all DAS antennas connected | This is just a question, "Are all the DAS antennas connected and working?" Testing cannot proceed without everything being hooked up and working.
4.1.5 | Fiber infrastructure make and model # | If there are fiber remotes, what is the fiber interface make and model number
4.1.6 | Number of fiber remotes | Document total number of fiber remotes connected to BDA through fiber interface
4.1.7 | Donor antenna location | Document location as well as any supplemental info to find and access donor antenna
4.1.8 | Donor antenna type | Yagi, Panel, Dish, Corner reflector, Omni
4.1.9 | Donor antenna gain (indicate dBd or dBi) | If known, required for new systems
4.1.10 | Max ERP from donor antenna | Sum BDA max output power, cable and connector loss, antenna gain, required for new systems
4.1.11 | Donor antenna azimuth | Degrees Clockwise from True North (0°) e.g., 90° is due East
4.1.12 | Expected donor site | Reference donor site names from "PSERN Technical Criteria Frequencies and Donor Sites", available at https://psern.org/confidential-resources/
4.1.13 | Inline attenuator value | If there is an inline attenuator on the donor line, document its value in dB here
4.2 | BDA Configuration:
4.2.1 | Verify filters | Refer to frequency lists in "PSERN Technical Criteria Frequencies and Donor Sites", available at https://psern.org/confidential-resources/ Wideband operation permitted for existing equipment. New construction or retrofits require channelized configuration, with a maximum channel width of 300 kHz and a maximum of 3 channels per filter.
4.2.2 | Configured DL gain | If different DL gain values are configured, document the greatest value
4.2.3 | Configured UL gain | If different UL gain values are configured, document the greatest value
4.2.5 | Verify UL AGC/ALC | If present as a feature. Required for new construction or new electronics.
4.2.6 | Verify UL squelch configured | If present as a feature. Required for new construction or new electronics.
4.3 | Isolation
4.3.1 | Isolation Results | If BDA supports self-reporting isolation, using that tool is acceptable. If not, • Connect Signal Generator to DAS cable infrastructure (cable disconnected from port on BDA labeled DAS/MOBILE/SVC) • Connect Spectrum Analyzer to Donor cable infrastructure (cable disconnected from port on BDA labeled DONOR/BTS) • If fiber infrastructure is present, confirm with DAS vendor input of +0dBm is acceptable for fiber point of interface • Generate test signal at XXX MHz at +0 dBm (or value confirmed with DAS vendor) • Identify receive of generated signal via donor antenna connected to spectrum analyzer • Document (Generated signal - measured value = isolation) e.g. (+0dBm - (-103dBm) = 103dB of isolation
4.3.1.1 | Isolation Diagram
4.4 | DL Testing
4.4.1 | DL receive at BDA donor input | Connect spectrum analyzer to cable from BDA donor port. Record dBm of control channel with spectrum analyzer resolution bandwidth of at least 15kHz but no more than 50kHz
4.4.1.1 | DL receive at BDA donor input diagram
4.4.2 | Calculated path loss from donor site | Refer to donor site ERP in "PSERN Technical Criteria Frequencies and Donor Sites", available at https://psern.org/confidential-resources/ If in-line attenuator is present on donor cable, be sure to include in measurement! Path loss = (Donor Site ERP) - (Control Channel dBm) For example, if Path loss = (+52dBm) - (-62dBm), Path loss = 114 dB
4.4.3 | BDA DL output | ****Must use at least 20dB 5W attenuator, connecting high power to spectrum analyzer**** With attenuator, connect spectrum analyzer to BDA DAS port Record dBm of control channel with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz. Don't forget to add the 20dB back in from the attenuator
4.4.3.1 | BDA DL output diagram
4.5 | Donor site UL testing
4.5.1 | RX noise floor value with DAS off | Connect spectrum analyzer to receive multicoupler at donor site. Set frequency span to entire uplink band, 806-817MHz Monitor noise floor and document received value
4.5.2 | BDA on/off test to verify no noise rise | Turn on DAS BDA confirm UL amplification with BDA software Reassess donor site spectrum analyzer for any appreciable noise floor rise None is acceptable
4.5.3 | Max UL receive | Connect spectrum analyzer to receive multicoupler at donor site. Set frequency span to entire uplink band, 806-817MHz Transmit for at least 10 seconds from hip height with a test radio directly under the closest DAS antenna Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz Any value greater than -75dBm not accepted
4.5.3.1 | Max/Min UL receive diagram
4.5.4 | Min UL receive | Connect spectrum analyzer to receive multicoupler at donor site. Set frequency span to entire uplink band, 806-817MHz To choose a minimum power transmission location, either ask DAS vendor to identify lowest DL receive area or choose a location equidistant between two DAS antennas Transmit for at least 10 seconds from hip height Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz No minimum value so long as DAQ is greater than 3.0
4.6 | DAS UL testing
4.6.1 | Measure max UL input to BDA | Connect spectrum analyzer to cable from BDA DAS port Transmit for at least 10 seconds from hip height with a test radio directly under the closest DAS antenna Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz
4.6.1.1 | Measure max/min UL input to BDA diagram
4.6.2 | Measure min UL input to BDA | Connect spectrum analyzer to cable from BDA DAS port To choose a minimum power transmission location, either ask DAS vendor to identify lowest DL receive area or choose a location equidistant between two DAS antennas Transmit for at least 10 seconds Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz
4.6.3 | Measure max UL output of BDA (verifying AGC) | ****Must use at least 20dB 5W attenuator, connecting high power to spectrum analyzer**** With attenuator, connect spectrum analyzer to BDA Donor port Transmit for at least 10 seconds from hip height with a test radio directly under the closest DAS antenna Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz Don't forget to add the 20dB back in to the dBm value from the attenuator Confirm UL AGC if configured is limiting output per channel
4.6.3.1 | Measure max/min UL output of BDA diagram
4.6.4 | Measure min UL output of BDA | ****Must use at least 20dB 5W attenuator, connecting high power to spectrum analyzer**** With attenuator, connect spectrum analyzer to BDA Donor port To choose a minimum power transmission location, either ask DAS vendor to identify lowest DL receive area or choose a location equidistant between two DAS antennas Record dBm of UL transmission with spectrum analyzer resolution bandwidth (RBW) of at least 15 kHz but no more than 50kHz Don't forget to add the 20dB back in to the dBm value from the attenuator
4.6.5 | Measure UL squelch | ****Must use at least 20dB 5W attenuator, connecting high power to spectrum analyzer**** Connect spectrum analyzer Set spectrum analyzer to wider than the entire uplink band, i.e. 800-825 MHz Compare the out-of-band noise floor output to the in-band noise. The system uplink gain should be diminished by the UL squelch value. (In-band Noise) - (Out-of-band Noise Floor) = Squelched uplink gain Squelched uplink gain should equal (uplink gain - squelch) e.g. (-50dBm) - (-95dBm) = Squelched UL Gain = 45dB UL Gain (75dB) - Squelch(30dB) = Squelched UL Gain= 45dB
4.6.5.1 | Measure UL squelch diagram
4.6.6 | Expected noise RX at Donor Site | Following setup of 4.6.5, document peak UL power with squelch applied, if applicable. UL noise ERP = (measured UL noise from BDA) - (cable and connector loss) + (donor antenna gain) Expected Noise RX at donor = (UL noise ERP) - (Path loss 4.4.2)
4.6.6 | Estimate max UL receive at donor site with calculated path loss | Max UL output (4.6.3) - Path loss (4.4.2) = Estimated Max UL receive compare to measured max UL receive from 4.5.3
4.6.7 | Estimate min UL receive at donor site with calculated path loss | Min UL output (4.6.4) - Path loss (4.4.2) = Estimated Min UL receive compare to measured min UL receive from 4.5.4
4.7 | TDI testing
4.7.1 | Comms check 3', 15', 30' from all emergency egress | TDI may manifest between the threshold of the DAS and the macro. DAQ of less than 3.0 indicates failure
4.7.2 | Test channel signal strength at 3' if 4.7.1 failure | Configure BDA with additional filter for test channel with same gain as other DL channels Generate test transmission on test channel to be amplified through DAS. Compare signal from DAS with Macro signal at TDI trouble locations. Dominant or near-dominant DAS signal at the exterior of the building is not allowed.
4.7.2.1 | Test channel signal strength test diagram
5 | Technician Sign-off
5.1 | DAS vendor point of contact name
5.2 | DAS vendor point of contact email
5.3 | Radio operator technician name
5.4 | Date
6 | Procedure for Rebroadcast Agreement execution

## Notes
Version | Last Revision
V 0.3 | 2021-05-27
Change Log
V 0.1 | Initial version
V 0.2 | Changed references of RSSI to dBm
V 0.3 | Changed columns for distribution to DAS vendors for comment, added a couple notes and additional items